## MAPA MODBUS RTU-TCP
|  | SISTEMA INTEGRADO DE GESTION |  |  |  |  | CODIGO: DDA-FT-012
VERSION: 001
MAPA MODBUS CILA-2S SRP
FECHA: 15-02-2022
PROTOCOLO: |  | MODBUS TCP/RTU |  |  |  |  | ODB:
VARIABLES DE LECTURA - TCP
Item | Nombre de Variable | Unidades | Minimo | Maximo | Dirrección MODBUS | TIPO | Tag SIERRACOL | ABB REGISTER
0 | Actual Speed | SPM*10 | 0 | 32650 | 0 | Holding R. (INT) | SI_XXXX1 | 400305
1 | Actual Motor Voltage | Volt | 0 | 32650 | 1 | Holding R. (INT) | EI_XXXX2 | 400110
2 | Rata de Producción (BPD) | BPD*10 | 0 | 32650 | 2 | Holding R. (INT) | FY_XXXX1 | 400321
3 | Motor Current | Amp*10 | 0 | 32650 | 3 | Holding R. (INT)
4 | Energia consumida por el motor (KWh) | KWh * 10 | 0 | 32650 | 4 | Holding R. (INT) | JI_XXXX1 | 400906
5 | Acel Ramp | Secs*10 | 0 | 32650 | 5 | Holding R. (INT)
6 | Decel Ramp | Secs*10 | 0 | 32650 | 6 | Holding R. (INT)
7 | Status SRP 0 - PUMP RUNNING 1 - PUMP STOPPED 2 - VSD ALARM 3 - GENERAL FAULT 4 - COMM. FAULT PF755 5 - TURNED OFF | Status CILA*10 | 0 | 32650 | 7 | Holding R. (INT) | YI_XXXX5 | 400215
8 | VSD Power KW | KW*10 | 0 | 32650 | 8 | Holding R. (INT)
9 | Min Speed Limit | HZ*10 | 0 | 32650 | 9 | Holding R. (INT)
10 | Contador KWh | KWh * 10 | 0 | 32650 | 10 | Holding R. (INT) | JI_XXXX3 | 400114
11 | Max Speed Limit | HZ*10 | 0 | 32650 | 11 | Holding R. (INT)
12 | Energia Regenerada KWh | KWh*10 | 0 | 32650 | 12 | Holding R. (INT) | JI_XXXX2 | 400907
13 | Direction 0 - Reverse 1 - Forward | unitless | 0 | 1 | 13 | Holding R. (INT)
14 | Reference Speed | HZ*10 | 0 | 32650 | 14 | Holding R. (INT)
15 | Potencia Instantanea | HP * 10 | 0 | 32650 | 15 | Holding R. (INT) | JI_XXXX4 | 400301
16 | DC Bus Voltage | Volt*10 | 0 | 32650 | 16 | Holding R. (INT) | EI_XXXX1 | 400108
17 | Potencia Nominal del Motor | HP * 10 | 0 | 32650 | 17 | Holding R. (INT) | JI_XXXX5 | 409909
18 | VSD Temperature | ºC*10 | 0 | 32650 | 18 | Holding R. (INT) | TI_XXXX1 | 400111
19 | Power Factor | *10 | 0 | 32650 | 19 | Holding R. (INT)
20 | Frecuencia del Motor | Hz * 10 | 0 | 32650 | 20 | Holding R. (INT) | SI_XXXX2 | 400103
21 | VFD Maximo (Velocidad Maxima del Balancin) | SPM * 10 | 0 | 32650 | 21 | Holding R. (INT) | SI_XXXX3 | 400121
22 | VFD Minimo (Velocidad Minima del balancín) | SPM * 10 | 0 | 32650 | 22 | Holding R. (INT) | SI_XXXX4 | 400002
23 | Torque del Motor (%) | % * 10 | 0 | 32650 | 23 | Holding R. (INT) | WI_XXXX1 | 400105
24 | Llenado de la bomba | % * 10 | 0 | 32650 | 24 | Holding R. (INT) | LI_XXXX1 | 32614
25 | Sumergencia total Instantanea | Ft | 0 | 32650 | 25 | Holding R. (INT) | LY_XXXX2 | 32222
26 | Reserved | unitless | 0 | 32650 | 26 | Holding R. (INT)
27 | Average Current | Amp*10 | 0 | 32650 | 27 | Holding R. (INT)
28 | Input Frecuency | HZ*10 | 0 | 32650 | 28 | Holding R. (INT)
29 | Average Kw | KW*10 | 0 | 32650 | 29 | Holding R. (INT)
30 | Average KVA | KVA*10 | 0 | 32650 | 30 | Holding R. (INT)
31 | Average KVAr | KVAr*10 | 0 | 32650 | 31 | Holding R. (INT)
32 | Input Power Factor | *10 | 0 | 32650 | 32 | Holding R. (INT)
33 | L1-L2 Voltage | Volts*10 | 0 | 32650 | 33 | Holding R. (INT)
34 | L2-L3 Voltage | Volts*10 | 0 | 32650 | 34 | Holding R. (INT)
35 | L1-L3 Voltage | Volts*10 | 0 | 32650 | 35 | Holding R. (INT)
36 | L1-N Voltage | Volts*10 | 0 | 32650 | 36 | Holding R. (INT)
37 | L2-N Voltage | Volts*10 | 0 | 32650 | 37 | Holding R. (INT)
38 | L3-N Voltage | Volts*10 | 0 | 32650 | 38 | Holding R. (INT)
39 | L1 Current | Amp*10 | 0 | 32650 | 39 | Holding R. (INT)
40 | L2 Current | Amp*10 | 0 | 32650 | 40 | Holding R. (INT)
41 | L3 Current | Amp*10 | 0 | 32650 | 41 | Holding R. (INT)
42 | L1 Power | KW*10 | 0 | 32650 | 42 | Holding R. (INT)
43 | L2 Power | KW*10 | 0 | 32650 | 43 | Holding R. (INT)
44 | L3 Power | KW*10 | 0 | 32650 | 44 | Holding R. (INT)
45 | Current Harmonics | %*10 | 0 | 32650 | 45 | Holding R. (INT)
46 | Voltage Harmonics | %*10 | 0 | 32650 | 46 | Holding R. (INT)
47 | Intake Pressure | psi | 0 | 32650 | 47 | Holding R. (INT) | PY_XXXX1 | 39703
48 | Discharge Pressure | psi | 0 | 32650 | 48 | Holding R. (INT)
49 | Intake Temperature | ºF | 0 | 32650 | 49 | Holding R. (INT)
50 | Discharge Temperature | psi | 0 | 32650 | 50 | Holding R. (INT)
51 | Reserved | NA | 0 | 32650 | 51 | Holding R. (INT)
52 | Casing Pressure | psi | 0 | 32650 | 52 | Holding R. (INT) | PIT_XXXX2 | 30063
53 | Tubing Head Pressure | psi | 0 | 32650 | 53 | Holding R. (INT) | PIT_XXXX1 | 30053
54 | Tubing Head Temperature | ºF | 0 | 32650 | 54 | Holding R. (INT)
55 | Voltage protection status | unitless | 0 | 32650 | 68 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
56 | Load protection status | unitless | 0 | 32650 | 69 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
57 | Reserved | NA | 0 | 32650 | 70 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
58 | Intake pressure protection status | unitless | 0 | 32650 | 71 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
59 | Intake temperature protection status | unitless | 0 | 32650 | 72 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
60 | Discharge pressure protection status | unitless | 0 | 32650 | 73 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
61 | Discharge temperature protection status | unitless | 0 | 32650 | 74 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
62 | Reserved | NA | 0 | 32650 | 75 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
63 | Tubing head pressure protection status | unitless | 0 | 32650 | 76 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
64 | Casing protection status | unitless | 0 | 32650 | 77 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
VARIABLES DE ESCRITURA - TCP
0 | Start - Bit 0 | unitless | 0 | 1 | 55.0 | Holding R. (INT) | YI_XXXX7 | 400001
1 | Stop - Bit 1 | unitless | 0 | 1 | 55.1 | Holding R. (INT) | YI_XXXX7 | 400001
2 | Reset - Bit 2 | unitless | 0 | 1 | 55.2 | Holding R. (INT) | YI_XXXX7 | 400001
3 | Reserved | unitless | 0 | 1 | 55.3 | Holding R. (INT)
4 | Reserved | unitless | 0 | 1 | 55.4 | Holding R. (INT)
4 | Speed reference | SPM*10 | 0 | 32650 | 56 | Holding R. (INT)
6 | Command direction | unitless | 0 | 32650 | 57 | Holding R. (INT) | 0: Forward, 1:Reverse
7 | Load HH setpoint | A | 0 | 32650 | 58 | Holding R. (INT)
8 | Load LL setpoint | A | 0 | 32650 | 59 | Holding R. (INT)
9 | Reserved | NA | 0 | 32650 | 60 | Holding R. (INT)
10 | Intake pressure HH setpoint | psi | 0 | 32650 | 61 | Holding R. (INT)
11 | Intake pressure LL setpoint | pis | 0 | 32650 | 62 | Holding R. (INT)
12 | Intake temperature HH setpoint | ºF | 0 | 32650 | 63 | Holding R. (INT)
13 | Discharge temperature HH setpoint | ºF | 0 | 32650 | 64 | Holding R. (INT)
14 | Reserved | NA | 0 | 32650 | 65 | Holding R. (INT)
15 | Accel ramp setpoint | s | 0 | 32650 | 66 | Holding R. (INT)
16 | Deccel ramp setpoint | s | 0 | 32650 | 67 | Holding R. (INT)